## Fume Hood Checkout
PHOENIX CONTROLS · ACM · Fume Hood Exhaust Valve · Checkout Sheet
Project | [5 empty] | ATS Job Number
Valve Tag # | [5 empty] | Date
Technician | [5 empty] | Description |  | Fume Hood Exhaust Valve
Model |  | Actuator Control Module (Critical Spaces Control Platform (CSCP))
Pass/Fail |  | Emer. Min |  | Valve Min |  |  | Valve Max
ACTUATOR CONTROL MODULE (ACM) — Wiring | [5 empty] | DHV BLACK BOX — Wiring
# | Interface |  | Point |  | Wiring | Point |  | Descriptor |  | Wiring
Connector/Terminal P10 | [5 empty] | TB1 — POWER IN
1 | Main Power Input |  | EGND (Jumper to Pin 2) |  |  | L1 + |  | 24 VAC
2 |  |  | V0 (Jumper to Pin 1) |  |  | GROUND
3 |  |  | +24VAC |  |  | L2 - |  | 24 VAC
Connector/Terminal P20 | [5 empty] | TB2 — OUTPUTS
4 | Actuator Output (Wired from Factory) |  | M1 |  |  | V OUT |  | Lands on Pin 27 on Phoenix Valve
5 |  |  | M2 |  |  | Ground |  | Lands on Pin 28 on Phoenix Valve
Connector/Terminal P30 | [5 empty] | TB3 — INPUTS (FHD500, 18-22 Gauge AWG)
13 | DP Sensor (Wired from Factory) |  | NC or Not Used |  |  | IN-1 + |  | Vertical Sash Sensor
14 |  |  | +3V3 |  |  | IN-1 - |  | Vertical Sash Sensor
15 |  |  | Ground |  |  | 24 VAC POWER
16 |  |  | Analog Input |  |  | HOT
Connector/Terminal P40 | [5 empty] | GND
18 | T1L Port A |  | DA+ |  |  | UIO 1
19 |  |  | DA- |  |  | Signal
20 |  |  | EGND |  |  | GND
Connector/Terminal P50 | [5 empty] | UIO 2
21 | T1L Port B |  | DA+ |  |  | Signal
22 |  |  | DA- |  |  | GND
23 |  |  | EGND |  |  | UI 1
Connector/Terminal P60 | [5 empty] | Signal
24 | RS485 |  | D- |  |  | GND
25 |  |  | D+ |  |  | UI 2
26 |  |  | COM (GND) |  |  | Signal
Connector/Terminal P70 | [5 empty] | GND
27 | UIO 1 & 2 |  | UIO_1 (Sash RED) |  |  | DO SWITCH
28 |  |  | GND (Sash BLACK) |  |  | DO +
29 |  |  | UIO_2 |  |  | DO -
30 |  |  | GND |  |  | MSTP
Connector/Terminal P80 | [5 empty] | RS485 +
27 | Vpot (Wired from Factory) |  | 5V |  |  | RS485 -
28 |  |  | VPOT |  |  | SASH SENSOR MOUNTING
29 |  |  | GND
FUME HOOD CHECKOUT — Configuration & Verification
Configuration |  |  |  | CFM |  |  |  | Height / Notes
Valve Min. | [7 empty] | NA
Valve Max. | [7 empty] | NA
Scheduled Min. | [7 empty] | NA
Scheduled Max. | [7 empty] | NA
Hood Sash Min. |  |  |  | NA
Hood Sash Max. |  |  |  | NA
Verification Task |  |  |  | Result / Pass / Fail |  |  |  | Height / Notes
Face Velocity @ 18"
Sash Height Alarm
Sash Sensor Output
Low Flow Alarm
JAM Alarm
Emergency Exhaust Override
NOTES
FHD500 BACNET POINTS
Type |  | ID |  | Name |  |  | Unit |  | Function | Access
MSV |  | 1 |  | HoodState |  |  |  |  | Live | R
AI |  | 1 |  | SashOpening |  |  | % |  | Live | R
AI |  | 2 |  | FaceVelocity |  |  | FPM |  | Live | R
AI |  | 3 |  | HoodCommand |  |  | CFM |  | Live | R
AI |  | 4 |  | FlowFdbk |  |  | CFM |  | Live | R
BI |  | 1 |  | OccupancyDetected |  |  |  |  | Live | R
BI |  | 2 |  | AlarmSashBroken |  |  |  |  | Live | R
BI |  | 3 |  | AlarmSashHeight |  |  |  |  | Live | R
BI |  | 4 |  | AlarmEmergencyExhaust |  |  |  |  | Live | R
BI |  | 5 |  | AlarmEnergyWaste |  |  |  |  | Live | R
AO |  | 1 |  | FlowCmdOverride |  |  | CFM |  | Config | RW
AO |  | 2 |  | FVCmdOverride |  |  | FPM |  | Config | RW
BO |  | 1 |  | RemoteEMExhaustOverride |  |  | mVolts/ohms |  | Config | RW
BO |  | 2 |  | HibernationOverride |  |  |  |  | Config | RW
AI |  | 200 |  | UIO1_PresentValue_In |  |  | %
AO |  | 200 |  | UIO1_PresentValue_Out |  |  | %
AI |  | 201 |  | UIO2_PresentValue_In |  |  | %
AO |  | 201 |  | UIO2_PresentValue_Out |  |  | %
AI |  | 202 |  | UI1_PresentValue_In |  |  | %
AI |  | 203 |  | UI2_PresentValue_In |  |  | %
BO |  | 200 |  | DO_PresentValue_Out
ACM BACNET POINTS
Type |  | ID |  | Name |  |  | Unit |  | Function | Access
BI |  | 1 |  | FlowAlarm |  |  | Alarm/Normal |  | Feedback | R
BI |  | 2 |  | JamAlarm |  |  | Alarm/Normal |  | Feedback | R
MSV |  | 1 |  | FSMStatus |  |  |  |  | Feedback | R
MSV |  | 2 |  | EmergencyMode | [5 empty] | R
MSV |  | 3 |  | ValvePositionStatus |  |  |  |  | Feedback | R
MSV |  | 4 |  | AcuatorStatus | [5 empty] | R
MSV |  | 5 |  | CurveStatus | [5 empty] | R
AO |  | 20 |  | FlowCmdOverride |  |  | CFM |  |  | RW
AO |  | 21 |  | VpotCmdOverride |  |  | Volt |  |  | RW
AI |  | 20 |  | FlowFdbk |  |  | CFM |  |  | R
AI |  | 21 |  | Vpot |  |  | Volt |  |  | R
AI |  | 22 |  | EffFlowSetpoint |  |  | CFM |  |  | R
AI |  | 200 |  | UIO1_PresentValue_In |  |  | % |  |  | R
AO |  | 200 |  | UIO1_PresentValue_Out |  |  | % |  |  | R
AI |  | 201 |  | UIO2_PresentValue_In |  |  | % |  |  | R
AO |  | 201 |  | UIO2_PresentValue_Out |  |  | % |  |  | R
AI |  | 202 |  | UIO3_PresentValue_In |  |  | % |  |  | R
▣ Amber = Factory wired — do not modify | [5 empty] | Light blue = Label ¦ White = Data entry field